## Instructions
Electrical Accident Emergency – Monitoring Workbook
Companion to the Electrical Accident Emergency SOP
How to use
Yellow cells, blue text | Input cells – type or pick from the drop-down. Only edit these.
Grey cells | Auto-calculated formulas – do not overwrite.
Green / amber / red | Status highlighting is applied automatically.
Sample data | Each register holds example rows from an Electrical Machines Lab scenario so the Dashboard shows results. Overwrite or clear before use.
Report date | Dashboard C5 defaults to TODAY(). Overwrite with a fixed date to report as of that date.
Sheets
Dashboard | SOP Section 20 KPIs with targets and automatic status, items needing attention, incidents by escalation level.
Escalation Classifier | SOP Section 10: answer yes/no questions to get Level 1–4 and who must be notified.
Immediate Checklist | SOP Section 22: 19-step checklist for a live incident, with completion tracking.
Incident Log | SOP Sections 3, 10 & 16: accidents, near misses and faults; isolation response time; RCA method; repeat flag.
CAPA Register | SOP Section 17: actions with due dates and effectiveness verification; closure counts only when verified.
LOTO Register | SOP Section 6: isolation, verification, lock/tag, re-energization authorization.
Inspection Schedule | SOP Sections 13 & 20: planned electrical inspections and tests; inspection compliance.
Reopening Clearance | SOP Section 19: lab may reopen only when all applicable conditions are met.
RACI Matrix | SOP Section 11: roles per activity, with an automatic check on accountability.
Training Records | SOP Section 15: role-based training, expiry and compliance.
Drill Register | Electrical safety drills planned vs completed.
Lists | Drop-down sources and adjustable parameters.
Core principle: No laboratory experiment, workshop activity, equipment operation, academic schedule, or research objective shall take precedence over human life and electrical safety.

## Dashboard
Electrical Safety – KPI Dashboard
SOP Section 20 – Key Performance Indicators (auto-calculated from the registers)
| Department / block | Department of EEE
| Report date | 2026-10-08
| Exposure measure (lab users in period) | 400
# | KPI | Formula | Actual | Target | Direction | Status | SOP target
1 | Electrical incident rate (per 100) | Accidents + faults ÷ exposure × 100 | 0.5 | 0.5 | Lower is better | On target | Declining
2 | Near-miss reporting rate (per 100) | Near misses ÷ exposure × 100 | 0.25 | 0.25 | Higher is better | On target | Increasing initially
3 | Avg emergency isolation response (min) | Isolation time − verified incident time | 3.3333 | 2 | Lower is better | Action needed | Minimized
4 | Electrical inspection compliance | Completed ÷ planned inspections due × 100 | 80% | 95% | Higher is better | Action needed | ≥ 95%
5 | Training compliance | Current ÷ personnel requiring training × 100 | 25% | 100% | Higher is better | Action needed | 100%
6 | Corrective action closure | CAPAs closed (verified) ÷ CAPAs due × 100 | 50% | 95% | Higher is better | Action needed | ≥ 95%
7 | Electrical safety drill completion | Completed ÷ planned drills due × 100 | 50% | 100% | Higher is better | Action needed | 100%
8 | Repeat incident rate | Repeat incidents ÷ total incidents × 100 | 33.33% | 0% | Lower is better | Action needed | Near zero
9 | LOTO compliance | Compliant ÷ LOTO applications × 100 | 50% | 100% | Higher is better | Action needed | Section 6
Numeric targets (yellow) are suggested where the SOP gives a direction only – set them to your institution's approved values.
| Items needing attention | Source | Count
| Overdue CAPAs | CAPA Register | 1
| CAPAs awaiting effectiveness verification | CAPA Register | 0
| Level 3–4 incidents logged | Incident Log | 0
| Isolation not by authorized person | Incident Log | 0
| Injuries without medical evaluation | Incident Log | 0
| Active LOTOs | LOTO Register | 1
| Non-compliant LOTOs | LOTO Register | 1
| Inspections missed | Inspection Schedule | 1
| Inspections failed | Inspection Schedule | 1
| Training expired / expiring / not trained | Training Records | 3
| Drills missed | Drill Register | 1
| Escalation level | Events logged
| Level 1 – Minor | 1
| Level 2 – Significant | 2
| Level 3 – Major | 0
| Level 4 – Critical | 0
Note on C5: Defaults to today. Overwrite with a fixed date to report as of that date.
Note on C6: Defined exposure measure for incident and near-miss rates, e.g. lab users or 1,000 lab-hours. Rates are per 100 units.

## Escalation Classifier
Electrical Accident Escalation Classifier
SOP Section 10 – life-threatening emergencies bypass intermediate levels
# | Question | Answer | Indicates
1 | Fatality or multiple casualties? | No | —
2 | Major fire or explosion? | No | —
3 | Major campus disruption? | No | —
4 | Serious injury (e.g. unconscious, cardiac effect, significant burn)? | No | —
5 | Major electrical fire? | No | —
6 | Significant operational disruption? | No | —
7 | Minor injury? | Yes | Level 2 – Significant
8 | Equipment damage? | Yes | Level 2 – Significant
9 | Localized fire or fault? | No | —
10 | Is anyone's life at immediate risk? | No | —
| Questions unanswered | 0
| Escalation level | Level 2 – Significant
| Response / notify | Laboratory/Workshop Supervisor + Safety Officer
| Immediate emergency call | As needed – follow standard reporting
Severity takes the highest level any 'Yes' indicates. Never touch a person still in contact with an energized source.

## Immediate Checklist
Electrical Accident – Immediate Checklist
SOP Section 22 – complete during and after the incident
Incident ref | EA-001
Location | Electrical Machines Lab
Date | 2026-09-18
Completed by | Lab In-Charge
# | Action | Done? | Time | Done by / remarks
1 | Stop work / experiment | Yes
2 | Raise emergency alarm | Yes
3 | Keep people away from the hazard | Yes
4 | Do not touch a person in contact with live electricity | Yes
5 | Isolate electrical energy safely | Yes
6 | Call emergency / medical assistance | Yes
7 | Confirm the area is safe before approaching the victim | Yes
8 | Provide appropriate first aid through trained personnel | Yes
9 | Control fire and secondary hazards | Yes
10 | Secure the affected area | Yes
11 | Notify the responsible authority | Yes
12 | Record the incident | Yes
13 | Preserve relevant evidence | Yes
14 | Conduct investigation | No
15 | Implement CAPA | No
16 | Verify corrective actions | No
17 | Authorize reopening | No
18 | Update risk register / SOP / training where required | No
19 | Record lessons learned for CQI | No
| Steps complete | 13
| Steps applicable | 19
| Completion | 68.42%
| Status | Follow-up in progress

## Incident Log
Electrical Incident & Near-Miss Log
SOP Sections 3, 10, 16 – every accident, significant fault, near miss, fire, arc flash or equipment-related injury
Ref | Date | Time verified | Time power isolated | Isolation response (min) | Location | Location type | Event type | Scenario | Equipment / circuit | Persons affected | Injury | Escalation level | Isolated by authorized person? | Medical evaluation done? | Fire involved? | RCA method | Root cause | CAPA ref | Repeat incident? | Lab reopened (date) | Description / remarks
EA-001 | 2026-09-18 | 10:42 | 10:44 | 2 | Electrical Machines Lab | Electrical / EEE lab | Accident | Electric shock | DC motor test bench terminal | 1 | Shock (no lasting injury) | Level 2 – Significant | Yes | Yes | No | 5 Why | Worn terminal shroud exposed live conductor | CA-001 | No | 2026-09-25 | Student touched exposed terminal during rewiring; supply isolated via emergency stop
EA-002 | 2026-09-29 | 14:05 | 14:06 | 1 | Power Electronics Lab | Electrical / EEE lab | Near miss | Overload | Bench socket strip | 0 | None | Level 1 – Minor | Yes | N/A | No | Equipment inspection | Unauthorized adapter overloading socket | CA-002 | No |  | Hot smell noticed; strip removed before damage
EA-003 | 2026-10-03 | 11:30 | 11:37 | 7 | Fabrication Area | Student project / fabrication area | Significant fault (no injury) | Damaged cable or plug | Soldering station lead | 0 | None | Level 2 – Significant | Yes | N/A | No | Maintenance-record review | Cable insulation damaged; not in inspection plan | CA-003 | Yes |  | Second cable fault in this area this term

## CAPA Register
Corrective & Preventive Action (CAPA) Register
SOP Section 17 – a CAPA counts as closed only when effectiveness is verified
CAPA ref | Incident ref | Finding | Corrective / preventive action | Responsible unit | Due date | Completed date | Effectiveness verification method | Verified effective? | Verified by | Status | Days overdue | Remarks
CA-001 | EA-001 | Faulty protective device | Replace terminal shrouds on all motor benches; add pre-start check | Maintenance | 2026-09-30 | 2026-09-24 | Functional test | Yes | Safety Officer | Closed
CA-002 | EA-002 | Overloaded socket | Remove unauthorized adapters; reconfigure bench load | Electrical Team | 2026-10-15 |  | Load verification |  |  | Due soon
CA-003 | EA-003 | Damaged cable | Replace cable and inspect similar equipment in fabrication area | Maintenance | 2026-10-06 |  | Inspection |  |  | Overdue | 2
CA-004 | EA-003 | Inadequate training | Conduct electrical safety training for fabrication-area users | Safety / IQAC | 2026-10-31 |  | Competency assessment |  |  | Open

## LOTO Register
Lockout / Tagout (LOTO) Register
SOP Section 6 – authorized isolation, stored energy considered, isolation verified, no unauthorized re-energization
LOTO no. | Date applied | Equipment / circuit | Isolation point | Authorized person | On authorized list? | Stored energy discharged? | Isolation verified (zero energy)? | Lock applied? | Tag applied? | Date removed | Re-energization authorized by | Inspected before return? | Compliance status | Status
LT-014 | 2026-09-18 | DC motor test bench 3 | DB-2 / MCB 7 | M. Suresh (Electrician) | Yes | Yes | Yes | Yes | Yes | 2026-09-24 | Lab In-Charge | Yes | Compliant | Closed
LT-015 | 2026-10-03 | Fabrication area socket ring | DB-5 / MCB 3 | R. Kumar (Technician) | Yes | N/A | No | Yes | Yes |  |  |  | Non-compliant | Active

## Inspection Schedule
Electrical Inspection & Testing Schedule
Electrical Inspection Compliance = completed ÷ planned inspections due to date (Section 20)
Asset / area | Location | Inspection type | Planned date | Date completed | Result | Inspection status | Interval (days) | Next due | Inspected by | Remarks
Main DB – EEE block | EEE block ground floor | Distribution board inspection | 2026-09-10 | 2026-09-10 | Pass | Completed | 180 | 2027-03-09 | Electrical Team
Electrical Machines Lab | EEE block | Earthing / grounding test | 2026-09-12 | 2026-09-12 | Pass | Completed | 365 | 2027-09-12 | Electrical Team
Electrical Machines Lab | EEE block | RCD / ELCB trip test | 2026-09-12 | 2026-09-13 | Pass | Completed | 90 | 2026-12-12 | Electrical Team
Motor test benches 1–6 | Electrical Machines Lab | Emergency stop test | 2026-09-20 | 2026-09-21 | Fail | Completed – failed | 30 | 2026-10-21 | Electrical Team | Bench 4 e-stop slow to trip – repaired and retested
Fabrication area | Workshop block | Cable & plug inspection | 2026-09-30 |  |  | Missed | 90 | 2026-12-29 | Electrical Team
Power Electronics Lab | EEE block | Portable appliance test | 2026-10-20 |  |  | Due soon | 180 | 2027-04-18 | Electrical Team
Formulas:
Next due = IF(OR([Planned date]="",[Interval (days)]=""),"",IF([Date completed]<>"",[Date completed],[Planned date])+[Interval (days)])

## Reopening Clearance
Laboratory / Workshop Reopening Clearance
SOP Section 19 – do not reopen merely because power has been restored
Incident ref | EA-001
Laboratory / workshop | Electrical Machines Lab
Serious incident (formal safety clearance needed)? | No
Clearance date | 2026-09-25
# | Reopening condition | Status | Verified by / remarks
1 | Electrical inspection completed | Yes
2 | Equipment inspection completed | Yes
3 | Protection-system verification | Yes
4 | Grounding / earthing verified | Yes
5 | Temporary hazards removed | Yes
6 | Corrective actions completed | Yes
7 | Authorization by competent authority | Yes
8 | Communication to users | Yes
9 | Reopening documented | Yes
10 | Formal safety clearance obtained (serious incidents) | N/A
| Conditions met / applicable | 9 / 9
| Decision | CLEARED TO REOPEN

## RACI Matrix
Roles & Responsibilities – RACI
SOP Section 11 – R Responsible · A Accountable · C Consulted · I Informed
Activity | Lab Faculty | Technician | Safety Officer | Maintenance / Electrical Team | Crisis Coordinator | Head of Institution | # Accountable | Check
Raise alarm | R | R | A | C | I | I | 1 | OK
Stop experiment / work | R | R | A | C | I | I | 1 | OK
Electrical isolation | C | C | A | R | I | I | 1 | OK
First aid coordination | R | C | A | I | C | I | 1 | OK
Area evacuation | R | R | A | C | C | I | 1 | OK
Emergency communication | C | I | C | I | R | A | 1 | OK
Equipment inspection | C | R | A | R | I | I | 1 | OK
Incident reporting | R | R | A | C | C | I | 1 | OK
Investigation | C | C | R | R | A | I | 1 | OK
CAPA | C | C | R | R | A | A | 2 | Shared accountability – confirm
Reopening authorization | C | C | R | R | A | A | 2 | Shared accountability – confirm
The SOP lists two Accountable roles for CAPA and Reopening authorization; the check flags these so the institution can confirm the intended sign-off.

## Training Records
Electrical Safety Training & Competency Records
SOP Section 15 – role-based and periodically refreshed
Name | ID / Staff no. | Role | Training required? | Training module | Date completed | Validity (months) | Expiry date | Status | Assessed competent? | Remarks
M. Suresh | EL-007 | Electrician | Yes | LOTO | 2026-03-10 | 12 | 2027-03-10 | Current | Yes
Dr. A. Rao | FA-112 | Lab Faculty | Yes | CPR / AED (designated personnel) | 2024-11-05 | 24 | 2026-11-05 | Expiring | Yes
R. Kumar | LT-021 | Technician | Yes | Electrical isolation | 2025-10-20 | 12 | 2026-10-20 | Expiring | Yes
K. Priya | 22A31A0412 | Student | Yes | Electrical hazard recognition |  | 12 |  | Not trained | No | Scheduled for next induction
Formulas:
Expiry date = IF(OR([Date completed]="",[Validity (months)]=""),"",EDATE([Date completed],[Validity (months)]))

## Drill Register
Electrical Safety Drill Register
Drill Completion = completed ÷ planned drills due to date (Section 20)
Planned date | Drill type | Laboratory / area | Conducted? | Date conducted | Participants | Isolation achieved (min) | Drill status | Observations / improvements
2026-08-20 | Electric shock response | Electrical Machines Lab | Yes | 2026-08-20 | 28 | 1.5 | Completed | Emergency stop location to be re-marked at bench height
2026-09-25 | Electrical fire evacuation | Fabrication Area | No |  |  |  | Missed
2026-11-12 | CPR / AED scenario | EEE block |  |  |  |  | Scheduled

## Lists
Yes / No | Yes / No / N/A | Pass / Fail | Accident scenario | Escalation level | Event type | Injury | Location type | RCA method | Inspection type | Training modules | Responsible unit | Drill type | RACI | Parameter | Value
Yes | Yes | Pass | Electric shock | Level 1 – Minor | Accident | None | Electrical / EEE lab | 5 Why | Earthing / grounding test | Electrical hazard recognition | Maintenance | Electric shock response | R | 'Due soon' window (days) | 14
No | No | Fail | Electrocution | Level 2 – Significant | Near miss | Shock (no lasting injury) | ECE lab | Fishbone / Ishikawa | RCD / ELCB trip test | Emergency shutdown | Electrical Team | Electrical fire evacuation | A | Training 'expiring' window (days) | 30
| N/A |  | Electrical burn | Level 3 – Major | Significant fault (no injury) | Burn | Computer / network lab | Fault Tree | Insulation resistance test | Electrical isolation | Lab | Emergency isolation | C
|  |  | Arc flash / arc blast | Level 4 – Critical |  | Arc-flash injury | Physics / applied science lab | Event timeline | Distribution board inspection | LOTO | Safety / IQAC | Arc-flash response | I
|  |  | Short circuit |  |  | Eye injury | Mechanical workshop | Equipment inspection | Cable & plug inspection | Fire response | Lab / Safety | CPR / AED scenario
|  |  | Overload |  |  | Hearing injury | R&D lab | Maintenance-record review | Emergency stop test | Emergency communication | Safety Officer | Tabletop exercise
|  |  | Exposed conductor |  |  | Cardiac effect | High-voltage lab |  | Portable appliance test | First aid awareness | Crisis Coordinator
|  |  | Damaged cable or plug |  |  | Secondary fall / impact | Battery / energy-storage lab |  | Thermographic survey | CPR / AED (designated personnel)
|  |  | Faulty electrical equipment |  |  | Fatality | Testing & measurement lab |  | Protective device verification | Lab-specific electrical hazards
|  |  | Electrical panel failure |  |  |  | Distribution panel / equipment room |  |  | Incident reporting
|  |  | Battery incident |  |  |  | Temporary experimental setup
|  |  | Water contacting electrical equipment |  |  |  | Maintenance / utility area
|  |  | Electrical fire |  |  |  | Student project / fabrication area
Improper grounding / earthing
Unauthorized electrical modification