## Instructions
Fire Prevention in HEIs – Monitoring Workbook
Companion to the Fire Prevention SOP
How to use
Yellow cells, blue text | Input cells – type or pick from the drop-down. Only edit these.
Grey cells | Auto-calculated formulas – do not overwrite.
Green / amber / red | Status highlighting is applied automatically. Dark red = critical / escalate.
Sample data | Registers hold example rows from a campus scenario so the Dashboard shows results. Overwrite or clear before use.
Report date | Dashboard C5 defaults to TODAY(). Overwrite with a fixed date to report as of that date.
Parameters | Risk thresholds and warning windows are on the Lists sheet (column R).
Sheets
Dashboard | SOP Section 17 KPIs plus supporting indicators, items needing attention and hazards by category.
Fire Risk Register | SOP Section 5: hazard, likelihood × consequence, risk level, controls, action owner and date, residual risk.
Inspection Checklist | SOP Section 13: 15 inspection items; critical life-safety deficiencies flagged for escalation.
Inspection Schedule | Planned vs completed inspections and critical deficiencies found – drives KPIs 17.1 and 17.5.
Hazard Reports & CAPA | SOP Section 15: record, assess, protect, assign, deadline, verify, update register, escalate.
Fire Protection Register | SOP Section 12: equipment service dates, impairments and interim controls – drives KPI 17.4.
Hot-Work Permits | SOP Section 11: the 10 permit conditions; work must STOP if any essential condition is not met.
Flammable Inventory | SOP Section 8: quantities vs permitted limits, approved storage, segregation, labelling, cylinders.
Hostel & Kitchen Checks | SOP Sections 9 and 10: residential and kitchen fire-prevention controls.
Training Records | SOP Section 14: training by role and module, expiry – drives KPI 17.3.
Fire Drill Register | Fire drill reports (Section 18 records).
RACI Matrix | SOP Section 16 with an automatic check that each activity has one Accountable role.
Lists | Drop-down sources and adjustable parameters.

## Dashboard
Fire Prevention – KPI Dashboard
SOP Section 17 – Fire Prevention KPIs (auto-calculated from the registers)
| Institution / campus | Main Campus
| Report date | 2026-10-10
# | KPI | Formula | Actual | Target | Direction | Status | Source
17.1 | Fire safety inspection compliance | Inspections completed ÷ inspections planned (due to date) × 100 | 75% | 95% | Higher is better | Action needed | Inspection Schedule
17.2 | Fire hazard closure rate | Hazards closed (verified) ÷ hazards reported × 100 | 20% | 90% | Higher is better | Action needed | Hazard Reports & CAPA
17.3 | Fire safety training compliance | Personnel with current training ÷ personnel requiring training × 100 | 40% | 95% | Higher is better | Action needed | Training Records
17.4 | Fire protection maintenance compliance | Equipment within service schedule ÷ equipment requiring service × 100 | 62.5% | 100% | Higher is better | Action needed | Fire Protection Register
17.5 | Critical fire safety deficiency rate | Critical deficiencies found ÷ inspections conducted (rate per inspection) | 0.33333 | 0 | Lower is better | Action needed | Inspection Schedule
S1 | High / critical residual fire risks | Fire Risk Register – residual level High or Critical | 0 | 0 | Lower is better | On target | Fire Risk Register
S2 | Flammable storage compliance | Compliant items ÷ inventory items × 100 | 60% | 100% | Higher is better | Action needed | Flammable Inventory
S3 | Hot-work permit compliance | Permits with all conditions met ÷ permits issued × 100 | 66.67% | 100% | Higher is better | Action needed | Hot-Work Permits
S4 | Fire drill completion | Drills completed ÷ drills planned (due to date) × 100 | 50% | 100% | Higher is better | Action needed | Fire Drill Register
17.1–17.5 are the SOP KPIs; S1–S4 are supporting indicators. Targets (yellow) are suggested – set them to your institution's approved values.
| Items needing attention | Source | Count
| Hazards to ESCALATE (critical open or overdue) | Hazard Reports & CAPA | 2
| Hazards awaiting effectiveness verification | Hazard Reports & CAPA | 1
| Critical deficiencies – latest checklist | Inspection Checklist | 1
| Non-compliant items – latest checklist | Inspection Checklist | 2
| Fire risk actions overdue | Fire Risk Register | 1
| Critical systems impaired with NO interim control | Fire Protection Register | 0
| Fire protection equipment impaired / service overdue | Fire Protection Register | 3
| Hot-work permits – STOP | Hot-Work Permits | 1
| Flammable items needing action | Flammable Inventory | 2
| Hostel non-compliances | Hostel & Kitchen Checks | 2
| Kitchen non-compliances | Hostel & Kitchen Checks | 0
| Inspections missed | Inspection Schedule | 1
| Training expired / expiring / not trained | Training Records | 3
| Fire drills missed | Fire Drill Register | 1
| Hazard category | Hazards reported
| Electrical | 0
| Laboratory | 0
| Kitchen | 1
| Storage | 1
| Hot Work | 0
| Smoking/Open Flames | 0
| Battery/Charging | 1
| Construction | 0
| Waste Management | 1
| Fire Protection | 1
Note on C5: Defaults to today. Overwrite with a fixed date to report as of that date.

## Fire Risk Register
Fire Risk Assessment Register
SOP Section 5 – hazards, risk ratings, existing controls, required actions, owners and completion dates
Ref | Area / location | Premises type | Hazard category | Hazard description | Likelihood (1-5) | Consequence (1-5) | Risk score | Risk level | Existing controls | Required action | Owner | Target date | Completed date | Residual likelihood | Residual consequence | Residual score | Residual level | Action status
FR-001 | Chemistry Lab 2 | Laboratory / research centre | Laboratory | Flammable solvents near hot plates | 3 | 4 | 12 | High | Flammables cabinet; supervised use | Relocate hot plates; set bench quantity limits | Laboratory In-charge | 2026-10-20 |  | 2 | 3 | 6 | Medium | Due soon
FR-002 | Boys Hostel B – rooms | Hostel / residential | Battery/Charging | Unapproved chargers and high-load heaters in rooms | 4 | 4 | 16 | Critical | Hostel rules; monthly warden rounds | Room inspections; confiscate prohibited devices; resident briefing | Hostel Warden | 2026-10-05 |  | 3 | 3 | 9 | Medium | Overdue
FR-003 | Central kitchen | Kitchen / cafeteria | Kitchen | Grease accumulation in hood and duct | 3 | 5 | 15 | Critical | Weekly hood cleaning | Quarterly duct cleaning by contractor | Canteen/Kitchen Supervisor | 2026-09-30 | 2026-09-28 | 2 | 4 | 8 | Medium | Complete
FR-004 | Main electrical room | Electrical room / server room / data centre | Electrical | Combustible storage near LT panel | 3 | 5 | 15 | Critical | Restricted access | Clear storage; mark keep-clear zone | Infrastructure/Maintenance Officer | 2026-10-15 |  | 1 | 4 | 4 | Low | Due soon
FR-005 | Library stack area | Library / auditorium / hall | Storage | Packaging and waste paper accumulation | 2 | 3 | 6 | Medium | Daily housekeeping |  | Department Head |  |  | 2 | 3 | 6 | Medium | No action required
Scoring guide
| Score | Likelihood of ignition / spread | Consequence
| 1 | Rare | Negligible – no injury, minor damage
| 2 | Unlikely | Minor – first aid, local damage
| 3 | Possible | Moderate – injury, room-level damage, disruption
| 4 | Likely | Major – serious injury, building damage, evacuation
| 5 | Almost certain | Severe – fatality, loss of critical facility
Assessment should consider occupancy, evacuation difficulty, life safety, critical infrastructure and adequacy of existing controls (Section 5).

## Inspection Checklist
Fire Safety Inspection Checklist
SOP Section 13 – any critical deficiency affecting life safety shall be escalated promptly
Building / area | Academic Block A
Inspection date | 2026-10-07
Inspected by | Fire and Safety Officer
# | Inspection item | Verification requirement | Status | Life-safety critical? | Escalation | Observation / action required | Owner / target date
1 | Electrical installations | No visible damage, unsafe connections or unresolved defects | Compliant |  | —
2 | Electrical panels | Accessible, protected and free from combustible storage | Non-compliant | No | Corrective action | Cartons stored beside DB-3 | Maintenance – 14-Oct
3 | Laboratories | Chemicals stored safely; equipment and ignition controls maintained | Compliant |  | —
4 | Kitchens | Cooking equipment, ventilation and fuel systems inspected | N/A |  | —
5 | Storage areas | Combustible materials controlled and chemicals appropriately stored | Compliant |  | —
6 | Escape routes | Corridors, staircases and exits unobstructed | Compliant |  | —
7 | Fire doors | Functional and not improperly wedged open | Non-compliant | Yes | ESCALATE NOW | Fire door to stair 2 wedged open with chair | Security Officer – immediate
8 | Fire equipment | Accessible, inspected and within service requirements | Compliant |  | —
9 | Detection and alarms | Testing and maintenance records current | Compliant |  | —
10 | Emergency lighting | Operational according to the inspection schedule | Compliant |  | —
11 | Waste | Combustible waste removed appropriately | Compliant |  | —
12 | Hot work | Required permits and controls in place | Compliant |  | —
13 | Contractors | Safety instructions and supervision provided | Compliant |  | —
14 | Training | Required personnel training current | Compliant |  | —
15 | Records | Defects documented and corrective actions tracked | Compliant |  | —
| Compliant |  | 12
| Non-compliant |  | 2
| Not applicable |  | 1
| Not yet assessed |  | 0
| Inspection compliance |  | 85.71%
| Critical deficiencies |  | 1
| Outcome |  | CRITICAL – escalate to Head of Institution

## Inspection Schedule
Fire Safety Inspection Schedule & Log
Drives KPI 17.1 Inspection Compliance and KPI 17.5 Critical Deficiency Rate
Area / building | Premises type | Inspection type | Planned date | Date conducted | Inspector | Items assessed | Items compliant | Compliance % | Critical deficiencies | Status | Remarks
Academic Block A | Academic block / classroom | Scheduled fire safety inspection | 2026-10-07 | 2026-10-07 | Fire and Safety Officer | 14 | 12 | 85.71% | 1 | Completed
Chemistry Lab 2 | Laboratory / research centre | Laboratory | 2026-09-22 | 2026-09-23 | Laboratory In-charge | 11 | 10 | 90.91% | 0 | Completed
Central kitchen | Kitchen / cafeteria | Kitchen / cafeteria | 2026-09-25 | 2026-09-25 | Canteen/Kitchen Supervisor | 9 | 9 | 100% | 0 | Completed
Boys Hostel B | Hostel / residential | Hostel | 2026-09-30 |  | Hostel Warden |  |  |  |  | Missed
Main electrical room | Electrical room / server room / data centre | Electrical installation | 2026-10-18 |  | Electrical Engineer/Authorized Technician |  |  |  |  | Due soon
Library | Library / auditorium / hall | Fire protection systems | 2026-11-05 |  | Fire and Safety Officer |  |  |  |  | Scheduled

## Hazard Reports & CAPA
Fire Hazard Reports & Corrective Action Register
SOP Section 15 – record → assess → protect → assign → deadline → verify → update register → escalate
Ref | Date reported | Location | Premises type | Hazard category | Description | Reported by | Severity | Immediate protective measures | Corrective action | Owner | Deadline | Date closed | Effectiveness verified? | Risk register updated? | Status | Escalate? | Days open
HZ-001 | 2026-09-12 | Boys Hostel B, Room 214 | Hostel / residential | Battery/Charging | E-scooter battery charging overnight in room | Hostel Warden | High | Charger removed; resident briefed | Provide designated charging area; update hostel rules | Hostel Warden | 2026-10-05 |  |  |  | Overdue | ESCALATE | 28
HZ-002 | 2026-09-18 | Central kitchen | Kitchen / cafeteria | Kitchen | Gas hose cracked near burner 3 | Canteen/Kitchen Supervisor | Critical | Gas supply isolated by technician | Replace hose; inspect all connections | Infrastructure/Maintenance Officer | 2026-09-20 | 2026-09-19 | Yes | Yes | Closed | — | 1
HZ-003 | 2026-10-07 | Academic Block A, stair 2 | Academic block / classroom | Fire Protection | Fire door wedged open | Fire and Safety Officer | Critical | Wedge removed; door closed | Install hold-open device linked to alarm or enforce closure | Infrastructure/Maintenance Officer | 2026-10-21 |  |  |  | Due soon | ESCALATE | 3
HZ-004 | 2026-10-07 | Academic Block A, DB-3 | Academic block / classroom | Storage | Cartons stored beside distribution board | Fire and Safety Officer | Medium | Cartons moved | Mark keep-clear zone; brief housekeeping | Security Officer | 2026-10-14 | 2026-10-09 |  |  | Awaiting verification | — | 2
HZ-005 | 2026-10-02 | Mechanical workshop | Workshop / store / maintenance | Waste Management | Oily rags in open bin | Faculty/Staff | Medium | Rags removed | Provide closed metal bin; daily disposal | Department Head | 2026-10-16 |  |  |  | Due soon | — | 8

## Fire Protection Register
Fire Protection Equipment & System Register
SOP Section 12 – inspection, testing and servicing; interim controls when a critical system is impaired
Asset ID | Equipment / system | Location | Last inspected / serviced | Service interval (days) | Next due | Functional? | Critical system? | Interim control in place (if impaired)? | Status | Serviced by | Remarks
FA-01 | Automatic fire detection system | Academic Block A | 2026-07-15 | 180 | 2027-01-11 | Yes | Yes |  | In service
MCP-A | Manual call point | Academic Block A – all floors | 2026-07-15 | 180 | 2027-01-11 | Yes | Yes |  | In service
EL-A | Emergency lighting | Academic Block A | 2026-09-01 | 30 | 2026-10-01 | Yes | Yes |  | Service overdue
FE-014 | Fire extinguisher | Chemistry Lab 2 | 2026-04-02 | 180 | 2026-09-29 | Yes | No |  | Service overdue |  | 6-monthly service missed
FE-022 | Fire extinguisher | Central kitchen | 2026-09-10 | 90 | 2026-12-09 | Yes | No |  | In service
HY-02 | Hydrant / hose system | Hostel B ground floor | 2026-08-20 | 90 | 2026-11-18 | No | Yes | Yes | Impaired – interim control |  | Pump pressure low; fire watch and extra extinguishers placed pending repair
SPR-L | Sprinkler / fixed suppression | Library stack area | 2026-06-30 | 180 | 2026-12-27 | Yes | Yes |  | In service
FD-S2 | Fire door / compartmentation | Academic Block A stair 2 | 2026-10-07 | 90 | 2027-01-05 | Yes | Yes |  | In service
Formulas:
Next due = IF(OR([Last inspected / serviced]="",[Service interval (days)]=""),"",[Last inspected / serviced]+[Service interval (days)])

## Hot-Work Permits
Hot-Work Permit Register
SOP Section 11 – hot work shall not be permitted where essential safety conditions cannot be achieved
Permit no. | Date | Location | Work type | Contractor / person | Authorization before work | Work area inspected | Combustibles removed / protected | Concealed & adjacent areas assessed | Fire-protection equipment provided | Competent fire watch assigned | Contractor competency verified | Cylinder & equipment safety | Post-work inspection done | Permit documented & closed | Pre-work check | Permit status
HW-031 | 2026-09-26 | Mechanical workshop | Welding | M/s Steelcraft | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | All conditions met | Closed
HW-032 | 2026-10-08 | Hostel B roof | Cutting | M/s Roofline | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | All conditions met | Authorized – open
HW-033 | 2026-10-09 | Library annex (renovation) | Grinding | M/s BuildRight | Yes | Yes | No | Yes | Yes | N/A | Yes | N/A |  |  | Conditions NOT met | STOP – do not permit

## Flammable Inventory
Flammable & Combustible Material Inventory
SOP Sections 7 & 8 – controlled quantities, approved storage, segregation, labelling, secured cylinders
Item ID | Material | Class | Location / store | Quantity held | Max permitted | Unit | Approved storage? | Segregated from ignition / incompatibles? | Labelled & closed? | Cylinder secured? (gas only) | Quantity check | Compliance | Remarks
FL-01 | Acetone | Flammable liquid | Chem Lab 2 – flammables cabinet | 8 | 10 | L | Yes | Yes | Yes | N/A | Within limit | Compliant
FL-02 | Ethanol | Flammable liquid | Chem Lab 2 – bench | 4 | 2 | L | No | Yes | Yes | N/A | Over limit | Action needed | Bench quantity exceeds limit; return excess to cabinet
FL-03 | LPG cylinders | Flammable gas cylinder | Central kitchen – cylinder bank | 6 | 8 | nos | Yes | Yes | Yes | Yes | Within limit | Compliant
FL-04 | Acetylene cylinder | Flammable gas cylinder | Mechanical workshop | 2 | 2 | nos | Yes | Yes | Yes | No | Within limit | Action needed | Chain missing on cylinder trolley
FL-05 | Paint thinner | Flammable liquid | Maintenance store | 15 | 20 | L | Yes | Yes | Yes | N/A | Within limit | Compliant

## Hostel & Kitchen Checks
Hostel & Kitchen Fire-Prevention Checks
SOP Sections 9 (residential facilities) and 10 (kitchens and cafeterias)
Hostel / residential facility – SOP Section 9
| Facility / date | Boys Hostel B | 2026-10-03
# | Control | Status | Remarks
1 | Periodic inspection of electrical wiring and appliances | Compliant
2 | Restrictions on unauthorized high-load electrical equipment | Non-compliant | Heaters found in 3 rooms
3 | Safe cooking arrangements; prohibited heating devices controlled | Compliant
4 | Charging equipment and batteries managed safely | Non-compliant | Scooter battery charged in room 214
5 | Unauthorized open flames and smoking prohibited | Compliant
6 | Combustible materials stored safely | Compliant
7 | Corridors, staircases and emergency exits unobstructed | Compliant
8 | Fire alarms and emergency lighting functioning | Compliant
9 | Fire-safety instructions visible | Compliant
10 | Orientation given to residents and hostel staff | Compliant
11 | Kitchens, common rooms and electrical areas inspected | Compliant
12 | Residents know how to report hazards and respond to alarms | Compliant
| Non-compliant items | 2
| Compliance | 83.33%
Kitchen / cafeteria – SOP Section 10
| Facility / date | Central kitchen | 2026-09-25
# | Control | Status | Remarks
1 | Cooking equipment inspected and maintained | Compliant
2 | Grease accumulation cleaned | Compliant
3 | Gas connections and fuel systems managed safely | Compliant
4 | Combustibles kept away from hot surfaces | Compliant
5 | Kitchen fire-protection equipment available | Compliant
6 | Ventilation maintained | Compliant
7 | Unauthorized cooking controlled | Compliant
8 | Staff know emergency shutdown and gas-leak procedure | Compliant
9 | Fuel installations inspected by competent personnel | Compliant
| Non-compliant items | 0
| Compliance | 100%

## Training Records
Fire Safety Training Records
SOP Section 14 – drives KPI 17.3 Training Compliance
Name | ID / Staff no. | Role | Training required? | Training module | Date completed | Validity (months) | Expiry date | Status | Practical (supervised)? | Remarks
S. Reddy | SO-001 | Fire and Safety Officer | Yes | Fire extinguisher use and limitations | 2026-02-10 | 12 | 2027-02-10 | Current | Yes
P. Lakshmi | HW-004 | Hostel Warden | Yes | Evacuation procedures | 2025-09-15 | 12 | 2026-09-15 | Expired | No
R. Naidu | KS-002 | Canteen/Kitchen Supervisor | Yes | Safe cooking and charging practices | 2025-11-01 | 12 | 2026-11-01 | Expiring | Yes
A. Kumar | SEC-11 | Security Officer | Yes | Fire alarm recognition | 2026-06-20 | 12 | 2027-06-20 | Current | No
M/s Steelcraft crew | CON-07 | Contractor/Vendor | Yes | Hot-work controls |  | 12 |  | Not trained | No
Formulas:
Expiry date = IF(OR([Date completed]="",[Validity (months)]=""),"",EDATE([Date completed],[Validity (months)]))

## Fire Drill Register
Fire Drill Register
Fire Drill Reports (SOP Section 18 records)
Planned date | Drill type | Building / area | Conducted? | Date conducted | Occupants present | Occupants accounted | Accountability % | Evacuation time (min) | Drill status | Observations / improvements
2026-08-28 | Building evacuation | Academic Block A | Yes | 2026-08-28 | 620 | 618 | 99.68% | 6.5 | Completed | Two students re-entered for belongings; repeat briefing
2026-09-24 | Hostel night evacuation | Boys Hostel B | No | [5 empty] | Missed
2026-11-14 | Kitchen fire | Central kitchen | [6 empty] | Scheduled

## RACI Matrix
Fire Prevention Roles & Responsibilities – RACI
SOP Section 16 – R Responsible · A Accountable · C Consulted · I Informed · A/R both
Activity | Head of Institution | Fire & Safety Officer | Infrastructure Team | Department / Lab Head | Security | # Accountable | Check
Approve fire-prevention policy | A | R | C | C | I | 1 | OK
Conduct fire-risk assessment | I | A/R | C | R | C | 1 | OK
Inspect electrical systems | I | C | A/R | C | I | 1 | OK
Control laboratory hazards | I | C | C | A/R | I | 1 | OK
Maintain fire-protection systems | I | A | R | C | C | 1 | OK
Conduct awareness training | I | A/R | C | R | C | 1 | OK
Report and record hazards | I | A | R | R | R | 1 | OK
Verify corrective actions | I | A/R | R | R | C | 1 | OK
Review fire-prevention performance | A | R | C | C | C | 1 | OK
The institution may adjust the RACI matrix to match its organizational structure and formally assigned authority (Section 16).

## Lists
Yes / No | Yes / No / N/A | Compliance | Premises type | Hazard category | Severity | Fire protection equipment | Roles | Training modules | Inspection type | Hot work type | Material class | Drill type | RACI | Score (1-5) | Parameter | Value
Yes | Yes | Compliant | Academic block / classroom | Electrical | Low | Automatic fire detection system | Head of Institution | Common causes of campus fires | Scheduled fire safety inspection | Welding | Flammable liquid | Building evacuation | R | 1 | Low risk: score up to | 4
No | No | Non-compliant | Laboratory / research centre | Laboratory | Medium | Manual call point | Fire and Safety Officer | Electrical and laboratory hazards | Electrical installation | Cutting | Flammable gas cylinder | Hostel night evacuation | A | 2 | Medium risk: score up to | 9
| N/A | N/A | Electrical room / server room / data centre | Kitchen | High | Audible / visual alarm | Infrastructure/Maintenance Officer | Safe storage of flammable materials | Laboratory | Grinding | Oxidizer | Laboratory fire | C | 3 | High risk: score up to | 14
|  |  | Library / auditorium / hall | Storage | Critical | Emergency lighting | Laboratory In-charge | Safe cooking and charging practices | Kitchen / cafeteria | Soldering | Combustible solid | Kitchen fire | I | 4 | 'Due soon' window (days) | 14
|  |  | Hostel / residential | Hot Work |  | Fire extinguisher | Electrical Engineer/Authorized Technician | Fire alarm recognition | Hostel | Brazing | Other hazardous | Tabletop exercise | A/R | 5 | Training 'expiring' window (days) | 30
|  |  | Kitchen / cafeteria | Smoking/Open Flames |  | Hydrant / hose system | Hostel Warden | Emergency reporting | Storage area | Other
|  |  | Workshop / store / maintenance | Battery/Charging |  | Sprinkler / fixed suppression | Canteen/Kitchen Supervisor | Evacuation procedures | Hot-work site
|  |  | Administrative office | Construction |  | Fire door / compartmentation | Security Officer | Fire extinguisher use and limitations | Contractor / construction site
|  |  | Transport / parking / vehicle workshop | Waste Management |  | Smoke-control system | Department Head | Hot-work controls | Fire protection systems
|  |  | Construction / renovation site | Fire Protection |  |  | Faculty/Staff | Contractor responsibilities
|  |  | Temporary structure / event venue |  |  |  | Student
Contractor/Vendor